## MIJ Annual Report
Michaelle Jean Annual Report Information
ECA # | 4191-ATBLYH
File | Michaelle Jean ECA
ECA item | Description | Status | Notes
a | Description of any operating problems encountered and corrective actions taken | Applicable
b | Summary of all maintenance carried out on any major structure, equipment, apparatus or thing formin part of all works on the property. | Applicable
c | Summary of any effluent quality or control measures undertaken for the reporting period. | Applicable
d | Summary and description of efforts made and results achieved in meeting the Effluent Objectives | Applicable
e | Summary of any complaints received during the reporting period and any steps taken to address the complaints | Applicable
f | Tabulation of the daily volume of effluent being treated by the works | N/A
g | Other information the District Manager requires | N/A
|  | Applicable | To be included, hasn't been started yet
|  | Started | Working on completion
|  | Pending | Requires more information - make note
|  | Complete | Finalized in report
|  | N/A | Not applicable for reporting period - make note if necessary

## MIJ Mixed Sewage Table
Sample Quality Parameter | Michaelle Jean Mixed Sewage
| pH | Temp | DO | BOD5 | TSS | TP | TKN | TAN
Units |  | ˚C | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
Sampling Date
2024-07-16 | 7.25 | 22.1 | 0.5 | 10 | 78 | 1.06 | 13 | 12.7
2024-08-20 | 7.45 | 23.4 | 1.33 | 10 | 53 | 0.6 | 6.3 | 6.2
2024-09-11 | 7.77 | 25 | 1.82 | 10 | 8 | 1.05 | 10.4 | 10.9
2024-10-31 | 7.53 | 19.2 | 4.93 | 62 | 27 | 4.91 | 66 | 64.7
2024-11-18 | 7.24 | 12.4 | 2.81 | 76 | 37 | 4.45 | 46.1 | 43.4
2024-12-11 | 8.19 | 10.2 | 1.85 | 62 | 58 | 6.72 | 80 | 60.8
2025-01-09 | 8.5 | 4.9 | 3.25 | 71 | 31 | 3.97 | 52.7 | 35.9
2025-02-06 | 7.25 | 7.2 | 0.24 | 166 | 117 | 6.75 | 76 | 70.4
2025-03-17 | 7.38 | 9.7 | 3.38 | 98 | 64 | 2.86 | 31.3 | 19.6
2025-04-10 | 7.55 | - | - | 72 | 55 | 5.86 | 71.3 | 73
2025-05-08 | 7.61 | 13.6 | 0.5 | 44 | 25 | 5.53 | 70.9 | 67.1
2025-06-18 08:20 | 7.71 | 17 | 0 | 37 | 20 | 4.98 | 58.5 | 55.6
2025-07-10 14:00 | 7.25 |  |  | 23 | 6 | 1.79 | 15.7 | 15.3
Mean | 7.5908 | 14.9727 | 1.8736 | 57 | 44.5385 | 3.8869 | 46.0154 | 41.2
Median | 7.53 | 13.6 | 1.82 | 62 | 37 | 4.45 | 52.7 | 43.4

## MIJ Biofilter Effluent Table
Sample Quality Parameter | Michaelle Jean Biofilter Effluent
| pH | Temp | DO | cBOD5 | TSS | TP | TKN | TAN | NO2 | NO3
Units |  | ˚C | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
Objectives |  |  |  | < 10 | < 10
Limits |  |  |  | 20 | 20
Sampling Date
2024-07-16 | 7.25 | 21.9 | 3.01 | 2 | 7 | 1.72 | 1 | 1.4 | 0.05 | 10.5
2024-08-20 | 7.29 | 22.8 | 3.3 | 2 | 2 | 0.95 | 0.5 | 0.2 | 0.03 | 7.61
2024-09-11 | 7.25 | 23.2 | 3.21 | 2 | 5 | 2.57 | 11.2 | 10.6 | 0.23 | 25.6
2024-10-31 | 7.27 | 18.1 | 6.25 | 2 | 4 | 4.22 | 16.5 | 16.8 | 0.03 | 35.3
2024-11-18 | 7.11 | 14.2 | 4.97 | 4 | 4 | 4.84 | 19.5 | 20.6 | 0.03 | 36.7
2024-12-11 | 7.22 | 10.5 | 2.74 | 2 | 12 | 5.52 | 23.8 | 23.4 | 0.03 | 36.1
2024-12-19 09:30 | - | - | - | - | 4 | - | - | - | - | -
2025-01-09 | 7.32 | 7.1 | 3.39 | 3 | 3 | 2.71 | 10.5 | 10.7 | 0.3 | 17.3
2025-02-06 | 7.68 | 7 | 1.77 | 5 | 4 | 5.3 | 28.8 | 26.7 | 0.03 | 28.5
2025-03-17 | 7.42 | 8.5 | 4.94 | 6 | 8 | 4.24 | 15.5 | 15.2 | 0.06 | 25.1
2025-04-10 | 7.28 | - | - | 4 | 7 | 5.18 | 25.1 | 25.5 | 0.3 | 26.6
2025-05-08 | 7.31 | 13.3 | 1.99 | 4 | 11 | 5.86 | 26.5 | 27.9 | 0.26 | 27.9
2025-06-18 08:20 | 7.02 | - | 3 | 3 | 5 | 5.99 | 26.7 | 27.9 | 0.1 | 25.7
2025-07-10 14:00 | 7.24 |  |  | 3 | 4 | 2.39 | 3.1 | 2.6 | 0.08 | 9.72
Mean | 7.2815 | 14.66 | 3.5064 | 3.2308 | 5.7143 | 3.9608 | 16.0538 | 16.1154 | 0.11769 | 24.0485
Median | 7.27 | 13.75 | 3.21 | 3 | 4.5 | 4.24 | 16.5 | 16.8 | 0.06 | 25.7
Final_Sheet
Meeting_Limits | TRUE |  |  | TRUE | TRUE
Meeting_Objectives | TRUE |  |  | TRUE | TRUE
cBOD_Limit | TRUE
cBOD_Objective | TRUE
TSS_Limit | TRUE
TSS_Objective | TRUE

## Apr 25
April 2025 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2025-04-01 | 10094997 | 5936 | 9818647 | 4705 | 10641
2025-04-02 | 10100793 | 5796 | 9829201 | 10554 | 16350
2025-04-03 | 10111039 | 10246 | 9834171 | 4970 | 15216
2025-04-04 | 10115519 | 4480 | 9844809 | 10638 | 15118
2025-04-05 | 10121495 | 5976 | 9849215 | 4406 | 10382
2025-04-06 | 10127288 | 5793 | 9849215 | 0 | 5793
2025-04-07 | 10131889 | 4601 | 9854962 | 5747 | 10348
2025-04-08 | 10137864 | 5975 | 9859871 | 4909 | 10884
2025-04-09 | 10143821 | 5957 | 9865180 | 5309 | 11266
2025-04-10 | 10150367 | 6546 | 9871014 | 5834 | 12380
2025-04-11 | 10156272 | 5905 | 9876450 | 5436 | 11341
2025-04-12 | 10156272 | 0 | 9881707 | 5257 | 5257
2025-04-13 | 10161171 | 4899 | 9881707 | 0 | 4899
2025-04-14 | 10178567 | 17396 | 9897833 | 16126 | 33522
2025-04-15 | 10189035 | 10468 | 9913999 | 16166 | 26634
2025-04-16 | 10194151 | 5116 | 9919833 | 5834 | 10950
2025-04-17 | 10199762 | 5611 | 9925626 | 5793 | 11404
2025-04-18 | 10204905 | 5143 | 9925626 | 0 | 5143
2025-04-19 | 10204905 | 0 | 9930396 | 4770 | 4770
2025-04-20 | 10209672 | 4767 | 9930396 | 0 | 4767
2025-04-21 | 10209672 | 0 | 9934944 | 4548 | 4548
2025-04-22 | 10214664 | 4992 | 9940454 | 5510 | 10502
2025-04-23 | 10220544 | 5880 | 9940454 | 0 | 5880
2025-04-24 | 10226427 | 5883 | 9945298 | 4844 | 10727
2025-04-25 | 10232279 | 5852 | 9950925 | 5627 | 11479
2025-04-26 | 10232279 | 0 | 9956450 | 5525 | 5525
2025-04-27 | 10237237 | 4958 | 9956450 | 0 | 4958
2025-04-28 | 10242935 | 5698 | 9961248 | 4798 | 10496
2025-04-29 | 10248565 | 5630 | 9966684 | 5436 | 11066
2025-04-30 | 10253687 | 5122 | 9971707 | 5023 | 10145
Total Flow (L) |  |  |  |  | 322391
Average Flow (L/day) |  |  |  |  | 10746
Typical Flow (L/day) |  |  |  |  | 10746

## Mar 25
March 2025 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2025-03-01 | 9955985 | 5714 | 9682632 | 0 | 5714
2025-03-02 | 9955985 | 0 | 9687454 | 4822 | 4822
2025-03-03 | 9960545 | 4560 | 9693269 | 5815 | 10375
2025-03-04 | 9966110 | 5565 | 9699078 | 5809 | 11374
2025-03-05 | 9977488 | 11378 | 9704974 | 5896 | 17274
2025-03-06 | 9982699 | 5211 | 9714516 | 9542 | 14753
2025-03-07 | 9987586 | 4887 | 9720406 | 5890 | 10777
2025-03-08 | 9992248 | 4662 | 9720406 | 0 | 4662
2025-03-09 | 9992248 | 0 | 9725203 | 4797 | 4797
2025-03-10 | 9997070 | 4822 | 9725203 | 0 | 4822
2025-03-11 | 9997070 | 0 | 9730883 | 5680 | 5680
2025-03-12 | 10002435 | 5365 | 9730883 | 0 | 5365
2025-03-13 | 10002435 | 0 | 9736380 | 5497 | 5497
2025-03-14 | 10007803 | 5368 | 9736380 | 0 | 5368
2025-03-15 | 10007803 | 0 | 9741724 | 5344 | 5344
2025-03-16 | 10012613 | 4810 | 9741724 | 0 | 4810
2025-03-17 | 10018068 | 5455 | 9747280 | 5556 | 11011
2025-03-18 | 10024006 | 5938 | 9752929 | 5649 | 11587
2025-03-19 | 10029991 | 5985 | 9763011 | 10082 | 16067
2025-03-20 | 10035803 | 5812 | 9768561 | 5550 | 11362
2025-03-21 | 10040949 | 5146 | 9773183 | 4622 | 9768
2025-03-22 | 10045626 | 4677 | 9773183 | 0 | 4677
2025-03-23 | 10045626 | 0 | 9777750 | 4567 | 4567
2025-03-24 | 10050510 | 4884 | 9783558 | 5808 | 10692
2025-03-25 | 10056338 | 5828 | 9788495 | 4937 | 10765
2025-03-26 | 10067207 | 10869 | 9793126 | 4631 | 15500
2025-03-27 | 10072273 | 5066 | 9798722 | 5596 | 10662
2025-03-28 | 10078211 | 5938 | 9803428 | 4706 | 10644
2025-03-29 | 10078211 | 0 | 9808604 | 5176 | 5176
2025-03-30 | 10083172 | 4961 | 9808604 | 0 | 4961
2025-03-31 | 10089061 | 5889 | 9813942 | 5338 | 11227
Total Flow (L) |  |  |  |  | 270100
Average Flow (L/day) |  |  |  |  | 8713
Typical Flow (L/day) |  |  |  |  | 8713

## Feb 25
February 2025 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2025-02-01 | 9815416 | 0 | 9546851 | 4425 | 4425
2025-02-02 | 9820053 | 4637 | 9546851 | 0 | 4637
2025-02-03 | 9825967 | 5914 | 9551467 | 4616 | 10530
2025-02-04 | 9832306 | 6339 | 9556046 | 4579 | 10918
2025-02-05 | 9838124 | 5818 | 9561432 | 5386 | 11204
2025-02-06 | 9838217 | 93 | 9566224 | 4792 | 4885
2025-02-07 | 9842731 | 4514 | 9572202 | 5978 | 10492
2025-02-08 | 9847754 | 5023 | 9572202 | 0 | 5023
2025-02-09 | 9847754 | 0 | 9576926 | 4724 | 4724
2025-02-10 | 9852505 | 4751 | 9582944 | 6018 | 10769
2025-02-11 | 9858246 | 5741 | 9587409 | 4465 | 10206
2025-02-12 | 9862735 | 4489 | 9593147 | 5738 | 10227
2025-02-13 | 9867453 | 4718 | 9593147 | 0 | 4718
2025-02-14 | 9873567 | 6114 | 9597828 | 4681 | 10795
2025-02-15 | 9873567 | 0 | 9603168 | 5340 | 5340
2025-02-16 | 9878627 | 5060 | 9603168 | 0 | 5060
2025-02-17 | 9878627 | 0 | 9608012 | 4844 | 4844
2025-02-18 | 9883520 | 4893 | 9613926 | 5914 | 10807
2025-02-19 | 9889530 | 6010 | 9619738 | 5812 | 11822
2025-02-20 | 9894762 | 5232 | 9625750 | 6012 | 11244
2025-02-21 | 9900334 | 5572 | 9631723 | 5973 | 11545
2025-02-22 | 9905584 | 5250 | 9631723 | 0 | 5250
2025-02-23 | 9905584 | 0 | 9636508 | 4785 | 4785
2025-02-24 | 9910422 | 4838 | 9642363 | 5855 | 10693
2025-02-25 | 9916065 | 5643 | 9648262 | 5899 | 11542
2025-02-26 | 9933652 | 17587 | 9658696 | 10434 | 28021
2025-02-27 | 9950271 | 16619 | 9676730 | 18034 | 34653
2025-02-28 | 9950271 | 0 | 9682632 | 5902 | 5902
Total Flow (L) |  |  |  |  | 275061
Average Flow (L/day) |  |  |  |  | 9824
Typical Flow (L/day) |  |  |  |  | 9824

## Jan 25
January 2025 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2025-01-01 | 9646877 | 4887 | 9367466 | 0 | 4887
2025-01-02 | 9646877 | 0 | 9372452 | 4986 | 4986
2025-01-03 | 9657348 | 10471 | 9378615 | 6163 | 16634
2025-01-04 | 9657348 | 0 | 9383151 | 4536 | 4536
2025-01-05 | 9661918 | 4570 | 9383151 | 0 | 4570
2025-01-06 | 9667798 | 5880 | 9387816 | 4665 | 10545
2025-01-07 | 9679518 | 11720 | 9405736 | 17920 | 29640
2025-01-08 | 9697157 | 17639 | 9416707 | 10971 | 28610
2025-01-09 | 9708578 | 11421 | 9433369 | 16662 | 28083
2025-01-10 | 9723205 | 14627 | 9449618 | 16249 | 30876
2025-01-11 | 9728154 | 4949 | 9449618 | 0 | 4949
2025-01-12 | 9728154 | 0 | 9454249 | 4631 | 4631
2025-01-13 | 9733263 | 5109 | 9460548 | 6299 | 11408
2025-01-14 | 9738184 | 4921 | 9466706 | 6158 | 11079
2025-01-15 | 9743192 | 5008 | 9472916 | 6210 | 11218
2025-01-16 | 9748137 | 4945 | 9478888 | 5972 | 10917
2025-01-17 | 9752805 | 4668 | 9485076 | 6188 | 10856
2025-01-18 | 9758013 | 5208 | 9485076 | 0 | 5208
2025-01-19 | 9758013 | 0 | 9489846 | 4770 | 4770
2025-01-20 | 9762764 | 4751 | 9495507 | 5661 | 10412
2025-01-21 | 9767562 | 4798 | 9501430 | 5923 | 10721
2025-01-22 | 9772070 | 4508 | 9507104 | 5674 | 10182
2025-01-23 | 9777120 | 5050 | 9513341 | 6237 | 11287
2025-01-24 | 9781782 | 4662 | 9513341 | 0 | 4662
2025-01-25 | 9781782 | 0 | 9518543 | 5202 | 5202
2025-01-26 | 9786559 | 4777 | 9518543 | 0 | 4777
2025-01-27 | 9792389 | 5830 | 9523091 | 4548 | 10378
2025-01-28 | 9798248 | 5859 | 9527781 | 4690 | 10549
2025-01-29 | 9804115 | 5867 | 9532230 | 4449 | 10316
2025-01-30 | 9809375 | 5260 | 9537959 | 5729 | 10989
2025-01-31 | 9815416 | 6041 | 9542426 | 4467 | 10508
Total Flow (L) |  |  |  |  | 348386
Average Flow (L/day) |  |  |  |  | 11238
Typical Flow (L/day) |  |  |  |  | 11238

## Dec 24
December 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-12-01 | 9515873 | 0 | 9254909 | 4693 | 4693
2024-12-02 | 9521404 | 5531 | 9260967 | 6058 | 11589
2024-12-03 | 9527488 | 6084 | 9267048 | 6081 | 12165
2024-12-04 | 9533010 | 5522 | 9273085 | 6037 | 11559
2024-12-05 | 9538094 | 5084 | 9278095 | 5010 | 10094
2024-12-06 | 9543256 | 5162 | 9283880 | 5785 | 10947
2024-12-07 | 9549484 | 6228 | 9283880 | 0 | 6228
2024-12-08 | 9549484 | 0 | 9288477 | 4597 | 4597
2024-12-09 | 9554655 | 5171 | 9294573 | 6096 | 11267
2024-12-10 | 9559576 | 4921 | 9300277 | 5704 | 10625
2024-12-11 | 9570476 | 10900 | 9300308 | 31 | 10931
2024-12-12 | 9576506 | 6030 | 9304939 | 4631 | 10661
2024-12-13 | 9582226 | 5720 | 9309376 | 4437 | 10157
2024-12-14 | 9582226 | 0 | 9314328 | 4952 | 4952
2024-12-15 | 9587132 | 4906 | 9314328 | 0 | 4906
2024-12-16 | 9593385 | 6253 | 9319110 | 4782 | 11035
2024-12-17 | 9599647 | 6262 | 9323750 | 4640 | 10902
2024-12-18 | 9605175 | 5528 | 9328776 | 5026 | 10554
2024-12-19 | 9611364 | 6189 | 9333608 | 4832 | 11021
2024-12-20 | 9616907 | 5543 | 9338402 | 4794 | 10337
2024-12-21 | 9616907 | 0 | 9343181 | 4779 | 4779
2024-12-22 | 9621844 | 4937 | 9343181 | 0 | 4937
2024-12-23 | 9621844 | 0 | 9348272 | 5091 | 5091
2024-12-24 | 9627138 | 5294 | 9348272 | 0 | 5294
2024-12-25 | 9627138 | 0 | 9353131 | 4859 | 4859
2024-12-26 | 9631704 | 4566 | 9353131 | 0 | 4566
2024-12-27 | 9631704 | 0 | 9357735 | 4604 | 4604
2024-12-28 | 9636650 | 4946 | 9357735 | 0 | 4946
2024-12-29 | 9636650 | 0 | 9362286 | 4551 | 4551
2024-12-30 | 9641990 | 5340 | 9362286 | 0 | 5340
2024-12-31 | 9641990 | 0 | 9367466 | 5180 | 5180
Total Flow (L) |  |  |  |  | 243367
Average Flow (L/day) |  |  |  |  | 7851
Typical Flow (L/day) |  |  |  |  | 7851

## Nov 24
November 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-11-01 | 9388574 | 0 | 9127237 | 4742 | 4742
2024-11-02 | 9394704 | 6130 | 9127237 | 0 | 6130
2024-11-03 | 9394704 | 0 | 9131745 | 4508 | 4508
2024-11-04 | 9399153 | 4449 | 9137437 | 5692 | 10141
2024-11-05 | 9403766 | 4613 | 9143082 | 5645 | 10258
2024-11-06 | 9409085 | 5319 | 9147559 | 4477 | 9796
2024-11-07 | 9419707 | 10622 | 9158283 | 10724 | 21346
2024-11-08 | 9424723 | 5016 | 9163898 | 5615 | 10631
2024-11-09 | 9429872 | 5149 | 9163898 | 0 | 5149
2024-11-10 | 9429872 | 0 | 9168603 | 4705 | 4705
2024-11-11 | 9435009 | 5137 | 9173965 | 5362 | 10499
2024-11-12 | 9440439 | 5430 | 9178584 | 4619 | 10049
2024-11-13 | 9445964 | 5525 | 9183637 | 5053 | 10578
2024-11-14 | 9451527 | 5563 | 9189231 | 5594 | 11157
2024-11-15 | 9456771 | 5244 | 9194195 | 4964 | 10208
2024-11-16 | 9461588 | 4817 | 9194195 | 0 | 4817
2024-11-17 | 9461588 | 0 | 9198903 | 4708 | 4708
2024-11-18 | 9467708 | 6120 | 9198931 | 28 | 6148
2024-11-19 | 9473884 | 6176 | 9205779 | 6848 | 13024
2024-11-20 | 9478953 | 5069 | 9214465 | 8686 | 13755
2024-11-21 | 9483966 | 5013 | 9220166 | 5701 | 10714
2024-11-22 | 9488443 | 4477 | 9220166 | 0 | 4477
2024-11-23 | 9488443 | 0 | 9220166 | 0 | 0
2024-11-24 | 9488443 | 0 | 9220166 | 0 | 0
2024-11-25 | 9493216 | 4773 | 9226203 | 6037 | 10810
2024-11-26 | 9497721 | 4505 | 9232240 | 6037 | 10542
2024-11-27 | 9502309 | 4588 | 9238209 | 5969 | 10557
2024-11-28 | 9506786 | 4477 | 9244231 | 6022 | 10499
2024-11-29 | 9511356 | 4570 | 9250216 | 5985 | 10555
2024-11-30 | 9515873 | 4517 | 9250216 | 0 | 4517
Total Flow (L) |  |  |  |  | 255020
Average Flow (L/day) |  |  |  |  | 8501
Typical Flow (L/day) |  |  |  |  | 9108

## Oct 24
October 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-10-01 | 9228229 | 5085 | 8973490 | 4511 | 9596
2024-10-02 | 9233177 | 4948 | 8979012 | 5522 | 10470
2024-10-03 | 9244250 | 11073 | 8983582 | 4570 | 15643
2024-10-04 | 9248745 | 4495 | 8988148 | 4566 | 9061
2024-10-05 | 9248745 | 0 | 8993417 | 5269 | 5269
2024-10-06 | 9253318 | 4573 | 8993417 | 0 | 4573
2024-10-07 | 9259457 | 6139 | 9003817 | 10400 | 16539
2024-10-08 | 9270205 | 10748 | 9009926 | 6109 | 16857
2024-10-09 | 9274987 | 4782 | 9015269 | 5343 | 10125
2024-10-10 | 9280260 | 5273 | 9020196 | 4927 | 10200
2024-10-11 | 9285952 | 5692 | 9025428 | 5232 | 10924
2024-10-12 | 9285952 | 0 | 9030371 | 4943 | 4943
2024-10-13 | 9290654 | 4702 | 9030371 | 0 | 4702
2024-10-14 | 9290654 | 0 | 9035027 | 4656 | 4656
2024-10-15 | 9301045 | 10391 | 9040645 | 5618 | 16009
2024-10-16 | 9306709 | 5664 | 9045587 | 4942 | 10606
2024-10-17 | 9312783 | 6074 | 9056188 | 10601 | 16675
2024-10-18 | 9318530 | 5747 | 9061864 | 5676 | 11423
2024-10-19 | 9323590 | 5060 | 9061864 | 0 | 5060
2024-10-20 | 9323590 | 0 | 9066424 | 4560 | 4560
2024-10-21 | 9335775 | 12185 | 9077151 | 10727 | 22912
2024-10-22 | 9346465 | 10690 | 9081693 | 4542 | 15232
2024-10-23 | 9351787 | 5322 | 9086525 | 4832 | 10154
2024-10-24 | 9357473 | 5686 | 9091159 | 4634 | 10320
2024-10-25 | 9362788 | 5315 | 9095775 | 4616 | 9931
2024-10-26 | 9362788 | 0 | 9100770 | 4995 | 4995
2024-10-27 | 9367790 | 5002 | 9100770 | 0 | 5002
2024-10-28 | 9372846 | 5056 | 9106366 | 5596 | 10652
2024-10-29 | 9377487 | 4641 | 9111287 | 4921 | 9562
2024-10-30 | 9383203 | 5716 | 9116572 | 5285 | 11001
2024-10-31 | 9388574 | 5371 | 9122495 | 5923 | 11294
Total Flow (L) |  |  |  |  | 318946
Average Flow (L/day) |  |  |  |  | 10289
Typical Flow (L/day) |  |  |  |  | 10289

## Sep 24
September 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-09-01 | 9091156 | 5026 | 8840802 | 0 | 5026
2024-09-02 | 9091156 | 0 | 8845211 | 4409 | 4409
2024-09-03 | 9095725 | 4569 | 8850138 | 4927 | 9496
2024-09-04 | 9101464 | 5739 | 8854778 | 4640 | 10379
2024-09-05 | 9107433 | 5969 | 8859881 | 5103 | 11072
2024-09-06 | 9113445 | 6012 | 8865012 | 5131 | 11143
2024-09-07 | 9119504 | 6059 | 8865012 | 0 | 6059
2024-09-08 | 9119504 | 0 | 8869649 | 4637 | 4637
2024-09-09 | 9128742 | 9238 | 8874290 | 4641 | 13879
2024-09-10 | 9134720 | 5978 | 8879322 | 5032 | 11010
2024-09-11 | 9140909 | 6189 | 8880287 | 965 | 7154
2024-09-12 | 9145527 | 4618 | 8884727 | 4440 | 9058
2024-09-13 | 9151318 | 5791 | 8889783 | 5056 | 10847
2024-09-14 | 9151318 | 0 | 8894220 | 4437 | 4437
2024-09-15 | 9156338 | 5020 | 8894220 | 0 | 5020
2024-09-16 | 9161030 | 4692 | 8899622 | 5402 | 10094
2024-09-17 | 9166818 | 5788 | 8905021 | 5399 | 11187
2024-09-18 | 9172260 | 5442 | 8910491 | 5470 | 10912
2024-09-19 | 9176894 | 4634 | 8920934 | 10443 | 15077
2024-09-20 | 9182916 | 6022 | 8920934 | 0 | 6022
2024-09-21 | 9182916 | 0 | 8926984 | 6050 | 6050
2024-09-22 | 9187640 | 4724 | 8926984 | 0 | 4724
2024-09-23 | 9193606 | 5966 | 8931926 | 4942 | 10908
2024-09-24 | 9198419 | 4813 | 8936444 | 4518 | 9331
2024-09-25 | 9202954 | 4535 | 8941395 | 4951 | 9486
2024-09-26 | 9208717 | 5763 | 8947284 | 5889 | 11652
2024-09-27 | 9213518 | 4801 | 8958267 | 10983 | 15784
2024-09-28 | 9218516 | 4998 | 8958267 | 0 | 4998
2024-09-29 | 9218516 | 0 | 8963173 | 4906 | 4906
2024-09-30 | 9223144 | 4628 | 8968979 | 5806 | 10434
Total Flow (L) |  |  |  |  | 265191
Average Flow (L/day) |  |  |  |  | 8840
Typical Flow (L/day) |  |  |  |  | 8840

## Aug 24
August 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-08-01 | 8963719 | 5483 | 8733480 | 4785 | 10268
2024-08-02 | 8973376 | 9657 | 8733480 | 0 | 9657
2024-08-03 | 8979123 | 5747 | 8739354 | 5874 | 11621
2024-08-04 | 8979123 | 0 | 8744207 | 4853 | 4853
2024-08-05 | 8984386 | 5263 | 8749005 | 4798 | 10061
2024-08-06 | 8990405 | 6019 | 8755011 | 6006 | 12025
2024-08-07 | 8995714 | 5309 | 8759577 | 4566 | 9875
2024-08-08 | 9000851 | 5137 | 8765032 | 5455 | 10592
2024-08-09 | 9005896 | 5045 | 8765032 | 0 | 5045
2024-08-10 | 9010669 | 4773 | 8769441 | 4409 | 9182
2024-08-11 | 9016286 | 5617 | 8775395 | 5954 | 11571
2024-08-12 | 9020720 | 4434 | 8780183 | 4788 | 9222
2024-08-13 | 9025203 | 4483 | 8784784 | 4601 | 9084
2024-08-14 | 9029733 | 4530 | 8789384 | 4600 | 9130
2024-08-15 | 9034173 | 4440 | 8794274 | 4890 | 9330
2024-08-16 | 9038770 | 4597 | 8799019 | 4745 | 9342
2024-08-17 | 9038770 | 0 | 8804011 | 4992 | 4992
2024-08-18 | 9044295 | 5525 | 8808655 | 4644 | 10169
2024-08-19 | 9050157 | 5862 | 8814445 | 5790 | 11652
2024-08-20 | 9055969 | 5812 | 8814495 | 50 | 5862
2024-08-21 | 9060751 | 4782 | 8814495 | 0 | 4782
2024-08-22 | 9060751 | 0 | 8820405 | 5910 | 5910
2024-08-23 | 9065944 | 5193 | 8820405 | 0 | 5193
2024-08-24 | 9065944 | 0 | 8825403 | 4998 | 4998
2024-08-25 | 9070627 | 4683 | 8825403 | 0 | 4683
2024-08-26 | 9070627 | 0 | 8829862 | 4459 | 4459
2024-08-27 | 9075656 | 5029 | 8829862 | 0 | 5029
2024-08-28 | 9075656 | 0 | 8835415 | 5553 | 5553
2024-08-29 | 9081271 | 5615 | 8835415 | 0 | 5615
2024-08-30 | 9081271 | 0 | 8840802 | 5387 | 5387
2024-08-31 | 9086130 | 4859 | 8840802 | 0 | 4859
Total Flow (L) |  |  |  |  | 240001
Average Flow (L/day) |  |  |  |  | 7742
Typical Flow (L/day) |  |  |  |  | 7742

## Jul 24
July 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-07-01 | 8808679 | 5950 | 8575712 | 5868 | 11818
2024-07-02 | 8814831 | 6152 | 8587592 | 11880 | 18032
2024-07-03 | 8819557 | 4726 | 8593537 | 5945 | 10671
2024-07-04 | 8831681 | 12124 | 8605685 | 12148 | 24272
2024-07-05 | 8837006 | 5325 | 8610128 | 4443 | 9768
2024-07-06 | 8841569 | 4563 | 8610128 | 0 | 4563
2024-07-07 | 8846598 | 5029 | 8615626 | 5498 | 10527
2024-07-08 | 8852716 | 6118 | 8621536 | 5910 | 12028
2024-07-09 | 8857248 | 4532 | 8626553 | 5017 | 9549
2024-07-10 | 8862258 | 5010 | 8631403 | 4850 | 9860
2024-07-11 | 8868293 | 6035 | 8637280 | 5877 | 11912
2024-07-12 | 8872884 | 4591 | 8642389 | 5109 | 9700
2024-07-13 | 8872884 | 0 | 8647162 | 4773 | 4773
2024-07-14 | 8878350 | 5466 | 8651873 | 4711 | 10177
2024-07-15 | 8884292 | 5942 | 8657738 | 5865 | 11807
2024-07-16 | 8893850 | 9558 | 8657772 | 34 | 9592
2024-07-17 | 8898334 | 4484 | 8663106 | 5334 | 9818
2024-07-18 | 8902884 | 4550 | 8668132 | 5026 | 9576
2024-07-19 | 8905777 | 2893 | 8672936 | 4804 | 7697
2024-07-20 | 8908385 | 2608 | 8677487 | 4551 | 7159
2024-07-21 | 8912871 | 4486 | 8682118 | 4631 | 9117
2024-07-22 | 8918717 | 5846 | 8687828 | 5710 | 11556
2024-07-23 | 8923170 | 4453 | 8693582 | 5754 | 10207
2024-07-24 | 8928337 | 5167 | 8698355 | 4773 | 9940
2024-07-25 | 8933274 | 4937 | 8702940 | 4585 | 9522
2024-07-26 | 8938065 | 4791 | 8707685 | 4745 | 9536
2024-07-27 | 8942878 | 4813 | 8707685 | 0 | 4813
2024-07-28 | 8947710 | 4832 | 8713099 | 5414 | 10246
2024-07-29 | 8953504 | 5794 | 8718985 | 5886 | 11680
2024-07-30 | 8958236 | 4732 | 8723866 | 4881 | 9613
2024-07-31 | 8958236 | 0 | 8728695 | 4829 | 4829
Total Flow (L) |  |  |  |  | 314358
Average Flow (L/day) |  |  |  |  | 10141
Typical Flow (L/day) |  |  |  |  | 10141

## Jun 24
June 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-06-01 | 8663945 | 0 | 8446437 | 5867 | 5867
2024-06-02 | 8668844 | 4899 | 8446437 | 0 | 4899
2024-06-03 | 8673950 | 5106 | 8451099 | 4662 | 9768
2024-06-04 | 8679173 | 5223 | 8456338 | 5239 | 10462
2024-06-05 | 8684326 | 5153 | 8461197 | 4859 | 10012
2024-06-06 | 8689191 | 4865 | 8466244 | 5047 | 9912
2024-06-07 | 8689191 | 0 | 8471924 | 5680 | 5680
2024-06-08 | 8694470 | 5279 | 8471924 | 0 | 5279
2024-06-09 | 8694470 | 0 | 8476672 | 4748 | 4748
2024-06-10 | 8699036 | 4566 | 8481528 | 4856 | 9422
2024-06-11 | 8704386 | 5350 | 8486601 | 5073 | 10423
2024-06-12 | 8709341 | 4955 | 8491534 | 4933 | 9888
2024-06-13 | 8714496 | 5155 | 8496871 | 5337 | 10492
2024-06-14 | 8719815 | 5319 | 8501906 | 5035 | 10354
2024-06-15 | 8724535 | 4720 | 8501906 | 0 | 4720
2024-06-16 | 8724535 | 0 | 8506436 | 4530 | 4530
2024-06-17 | 8735031 | 10496 | 8518131 | 11695 | 22191
2024-06-18 | 8745388 | 10357 | 8518171 | 40 | 10397
2024-06-19 | 8751601 | 6213 | 8523567 | 5396 | 11609
2024-06-20 | 8756155 | 4554 | 8534476 | 10909 | 15463
2024-06-21 | 8761671 | 5516 | 8538959 | 4483 | 9999
2024-06-22 | 8766533 | 4862 | 8538959 | 0 | 4862
2024-06-23 | 8766533 | 0 | 8543457 | 4498 | 4498
2024-06-24 | 8771562 | 5029 | 8548887 | 5430 | 10459
2024-06-25 | 8776116 | 4554 | 8554323 | 5436 | 9990
2024-06-26 | 8781481 | 5365 | 8554323 | 0 | 5365
2024-06-27 | 8787423 | 5942 | 8559154 | 4831 | 10773
2024-06-28 | 8792782 | 5359 | 8564504 | 5350 | 10709
2024-06-29 | 8797758 | 4976 | 8569844 | 5340 | 10316
2024-06-30 | 8802729 | 4971 | 8569844 | 0 | 4971
Total Flow (L) |  |  |  |  | 268058
Average Flow (L/day) |  |  |  |  | 8935
Typical Flow (L/day) |  |  |  |  | 8935

## May 24
May 2024 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-05-01 | 8530529 | 8482 | 8297096 | 5732 | 14214
2024-05-02 | 8536082 | 5553 | 8306966 | 9870 | 15423
2024-05-03 | 8546886 | 10804 | 8312679 | 5713 | 16517
2024-05-04 | 8546886 | 0 | 8317366 | 4687 | 4687
2024-05-05 | 8551474 | 4588 | 8317366 | 0 | 4588
2024-05-06 | 8557240 | 5766 | 8322521 | 5155 | 10921
2024-05-07 | 8561797 | 4557 | 8328250 | 5729 | 10286
2024-05-08 | 8566351 | 4554 | 8333831 | 5581 | 10135
2024-05-09 | 8571176 | 4825 | 8339260 | 5429 | 10254
2024-05-10 | 8576079 | 4903 | 8344764 | 5504 | 10407
2024-05-11 | 8576079 | 0 | 8349667 | 4903 | 4903
2024-05-12 | 8580624 | 4545 | 8349667 | 0 | 4545
2024-05-13 | 8585440 | 4816 | 8354874 | 5207 | 10023
2024-05-14 | 8590494 | 5054 | 8360428 | 5554 | 10608
2024-05-15 | 8595455 | 4961 | 8366144 | 5716 | 10677
2024-05-16 | 8600228 | 4773 | 8371913 | 5769 | 10542
2024-05-17 | 8605146 | 4918 | 8377670 | 5757 | 10675
2024-05-18 | 8605146 | 0 | 8382587 | 4917 | 4917
2024-05-19 | 8609693 | 4547 | 8382587 | 0 | 4547
2024-05-20 | 8609693 | 0 | 8384740 | 2153 | 2153
2024-05-21 | 8621404 | 11711 | 8392793 | 8053 | 19764
2024-05-22 | 8626124 | 4720 | 8398608 | 5815 | 10535
2024-05-23 | 8631261 | 5137 | 8404350 | 5742 | 10879
2024-05-24 | 8635951 | 4690 | 8410162 | 5812 | 10502
2024-05-25 | 8635951 | 0 | 8415690 | 5528 | 5528
2024-05-26 | 8640610 | 4659 | 8415690 | 0 | 4659
2024-05-27 | 8641658 | 1048 | 8424829 | 9139 | 10187
2024-05-28 | 8647495 | 5837 | 8429531 | 4702 | 10539
2024-05-29 | 8652385 | 4890 | 8435204 | 5673 | 10563
2024-05-30 | 8658182 | 5797 | 8440570 | 5366 | 11163
2024-05-31 | 8663945 | 5763 | 8440570 | 0 | 5763
Total Flow (L) |  |  |  |  | 291104
Average Flow (L/day) |  |  |  |  | 9390
Typical Flow (L/day) |  |  |  |  | 9390

## Apr 24
April 2024 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-04-01 | 0 | 4471 | 4471
2024-04-02 | 8988 | 4958 | 13946
2024-04-03 | 5371 | 11091 | 16462
2024-04-04 | 5292 | 5291 | 10583
2024-04-05 | 5331 | 5004 | 10335
2024-04-06 | 4908 | 0 | 4908
2024-04-07 | 0 | 4536 | 4536
2024-04-08 | 4514 | 0 | 4514
2024-04-09 | 4958 | 5692 | 10650
2024-04-10 | 5072 | 4507 | 9579
2024-04-11 | 4669 | 9664 | 14333
2024-04-12 | 4862 | 5784 | 10646
2024-04-13 | 4677 | 0 | 4677
2024-04-14 | 0 | 5713 | 5713
2024-04-15 | 5489 | 5393 | 10882
2024-04-16 | 9650 | 5177 | 14827
2024-04-17 | 5902 | 5242 | 11144
2024-04-18 | 5769 | 5944 | 11713
2024-04-19 | 4822 | 4940 | 9762
2024-04-20 | 4931 | 0 | 4931
2024-04-21 | 0 | 4511 | 4511
2024-04-22 | 4492 | 4933 | 9425
2024-04-23 | 5276 | 5257 | 10533
2024-04-24 | 5713 | 5754 | 11467
2024-04-25 | 5531 | 5670 | 11201
2024-04-26 | 11766 | 5757 | 17523
2024-04-27 | 5853 | 5713 | 11566
2024-04-28 | 4547 | 5202 | 9749
2024-04-29 | 5871 | 10338 | 16209
2024-04-30 | 7712 | 5806 | 13518
Total Flow (L) |  |  | 304314
Average Flow (L/day) |  |  | 10144
Typical Flow (L/day) |  |  | 10144

## Mar 24
March 2024 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-03-01 | 11655 | 11729 | 23384
2024-03-02 | 0 | 4520 | 4520
2024-03-03 | 4551 | 0 | 4551
2024-03-04 | 4609 | 4613 | 9222
2024-03-05 | 4530 | 9456 | 13986
2024-03-06 | 5901 | 5957 | 11858
2024-03-07 | 5865 | 5889 | 11754
2024-03-08 | 10517 | 5926 | 16443
2024-03-09 | 0 | 5649 | 5649
2024-03-10 | 5171 | 0 | 5171
2024-03-11 | 4856 | 5566 | 10422
2024-03-12 | 0 | 5836 | 5836
2024-03-13 | 9262 | 19 | 9281
2024-03-14 | 0 | 5781 | 5781
2024-03-15 | 10709 | 5806 | 16515
2024-03-16 | 0 | 4477 | 4477
2024-03-17 | 4622 | 4859 | 9481
2024-03-18 | 5500 | 5338 | 10838
2024-03-19 | 17606 | 11695 | 29301
2024-03-20 | 5482 | 5636 | 11118
2024-03-21 | 5621 | 4770 | 10391
2024-03-22 | 4860 | 5331 | 10191
2024-03-23 | 0 | 5260 | 5260
2024-03-24 | 4514 | 0 | 4514
2024-03-25 | 5571 | 5529 | 11100
2024-03-26 | 5353 | 0 | 5353
2024-03-27 | 0 | 4942 | 4942
2024-03-28 | 5146 | 4604 | 9750
2024-03-29 | 5386 | 0 | 5386
2024-03-30 | 0 | 5210 | 5210
2024-03-31 | 4511 | 0 | 4511
Total Flow (L) |  |  | 296196
Average Flow (L/day) |  |  | 9555
Typical Flow (L/day) |  |  | 9555

## Feb 24
February 2024 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-02-01 | 5541 | 5359 | 10900
2024-02-02 | 4665 | 5313 | 9978
2024-02-03 | 0 | 5553 | 5553
2024-02-04 | 0 | 0 | 0
2024-02-05 | 5960 | 5846 | 11806
2024-02-06 | 5229 | 5920 | 11149
2024-02-07 | 4484 | 5911 | 10395
2024-02-08 | 4477 | 5852 | 10329
2024-02-09 | 4816 | 5615 | 10431
2024-02-10 | 5883 | 0 | 5883
2024-02-11 | 0 | 4988 | 4988
2024-02-12 | 5944 | 0 | 5944
2024-02-13 | 5988 | 4465 | 10453
2024-02-14 | 5902 | 5680 | 11582
2024-02-15 | 4807 | 5519 | 10326
2024-02-16 | 5772 | 4693 | 10465
2024-02-17 | 0 | 5833 | 5833
2024-02-18 | 4686 | 0 | 4686
2024-02-19 | 0 | 0 | 0
2024-02-20 | 6010 | 10129 | 16139
2024-02-21 | 5365 | 0 | 5365
2024-02-22 | 5935 | 5655 | 11590
2024-02-23 | 5970 | 5679 | 11649
2024-02-24 | 0 | 4499 | 4499
2024-02-25 | 4514 | 0 | 4514
2024-02-26 | 5916 | 5063 | 10979
2024-02-27 | 5646 | 5232 | 10878
2024-02-28 | 5587 | 5550 | 11137
2024-02-29 | 4912 | 5905 | 10817
Total Flow (L) |  |  | 248268
Average Flow (L/day) |  |  | 8561
Typical Flow (L/day) |  |  | 9195

## Jan 24
January 2024 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2024-01-01 | 0 | 5316 | 5316
2024-01-02 | 5858 | 0 | 5858
2024-01-03 | 0 | 5639 | 5639
2024-01-04 | 4496 | 0 | 4496
2024-01-05 | 0 | 4502 | 4502
2024-01-06 | 0 | 0 | 0
2024-01-07 | 5519 | 0 | 5519
2024-01-08 | 5368 | 4905 | 10273
2024-01-09 | 0 | 5883 | 5883
2024-01-10 | 4520 | 5966 | 10486
2024-01-11 | 5871 | 5884 | 11755
2024-01-12 | 4474 | 5861 | 10335
2024-01-13 | 4952 | 0 | 4952
2024-01-14 | 0 | 5118 | 5118
2024-01-15 | 4480 | 5501 | 9981
2024-01-16 | 4486 | 4896 | 9382
2024-01-17 | 4785 | 5797 | 10582
2024-01-18 | 4521 | 5698 | 10219
2024-01-19 | 4939 | 5905 | 10844
2024-01-20 | 5750 | 0 | 5750
2024-01-21 | 0 | 0 | 0
2024-01-22 | 5486 | 5876 | 11362
2024-01-23 | 4871 | 5461 | 10332
2024-01-24 | 5612 | 4875 | 10487
2024-01-25 | 4505 | 5195 | 9700
2024-01-26 | 4529 | 0 | 4529
2024-01-27 | 0 | 5439 | 5439
2024-01-28 | 4628 | 0 | 4628
2024-01-29 | 5455 | 4468 | 9923
2024-01-30 | 5547 | 5565 | 11112
2024-01-31 | 5901 | 4964 | 10865
Total Flow (L) |  |  | 235267
Average Flow (L/day) |  |  | 7589
Typical Flow (L/day) |  |  | 8113

## Dec 23
December 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-12-01 | 11372 | 4779 | 16151
2023-12-02 | 0 | 4866 | 4866
2023-12-03 | 6095 | 0 | 6095
2023-12-04 | 5939 | 8451 | 14390
2023-12-05 | 5442 | 8307 | 13749
2023-12-06 | 10123 | 5938 | 16061
2023-12-07 | 5571 | 4974 | 10545
2023-12-08 | 5957 | 5442 | 11399
2023-12-09 | 0 | 5497 | 5497
2023-12-10 | 5951 | 0 | 5951
2023-12-11 | 5892 | 10308 | 16200
2023-12-12 | 5393 | 5368 | 10761
2023-12-13 | 5356 | 5399 | 10755
2023-12-14 | 5063 | 5954 | 11017
2023-12-15 | 5621 | 5935 | 11556
2023-12-16 | 5577 | 0 | 5577
2023-12-17 | 0 | 5819 | 5819
2023-12-18 | 16826 | 13169 | 29995
2023-12-19 | 22989 | 20467 | 43456
2023-12-20 | 11976 | 14979 | 26955
2023-12-21 | 22925 | 18860 | 41785
2023-12-22 | 5254 | 4644 | 9898
2023-12-23 | 0 | 0 | 0
2023-12-24 | 0 | 5796 | 5796
2023-12-25 | 5614 | 0 | 5614
2023-12-26 | 0 | 0 | 0
2023-12-27 | 0 | 5769 | 5769
2023-12-28 | 4912 | 0 | 4912
2023-12-29 | 0 | 4462 | 4462
2023-12-30 | 5214 | 0 | 5214
2023-12-31 | 0 | 0 | 0
Total Flow (L) |  |  | 360245
Average Flow (L/day) |  |  | 11621
Typical Flow (L/day) |  |  | 12866

## Nov 23
November 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-11-01 | 4406 | 9725 | 14131
2023-11-02 | 10677 | 4819 | 15496
2023-11-03 | 5563 | 5479 | 11042
2023-11-04 | 4696 | 5486 | 10182
2023-11-05 | 0 | 4421 | 4421
2023-11-06 | 10079 | 5285 | 15364
2023-11-07 | 5571 | 5368 | 10939
2023-11-08 | 15812 | 10357 | 26169
2023-11-09 | 21250 | 22591 | 43841
2023-11-10 | 6417 | 4425 | 10842
2023-11-11 | 0 | 5381 | 5381
2023-11-12 | 5217 | 0 | 5217
2023-11-13 | 11880 | 15842 | 27722
2023-11-14 | 5396 | 5136 | 10532
2023-11-15 | 9724 | 5319 | 15043
2023-11-16 | 5439 | 9629 | 15068
2023-11-17 | 5874 | 0 | 5874
2023-11-18 | 0 | 5837 | 5837
2023-11-19 | 4807 | 0 | 4807
2023-11-20 | 5368 | 5492 | 10860
2023-11-21 | 4721 | 4495 | 9216
2023-11-22 | 5790 | 5948 | 11738
2023-11-23 | 6059 | 5827 | 11886
2023-11-24 | 5282 | 5409 | 10691
2023-11-25 | 0 | 5565 | 5565
2023-11-26 | 4726 | 0 | 4726
2023-11-27 | 4632 | 10659 | 15291
2023-11-28 | 8892 | 6105 | 14997
2023-11-29 | 4853 | 11745 | 16598
2023-11-30 | 4526 | 6280 | 10806
Total Flow (L) |  |  | 380282
Average Flow (L/day) |  |  | 12676
Typical Flow (L/day) |  |  | 12676

## Oct 23
October 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-10-01 | 0 | 0 | 0
2023-10-02 | 5581 | 5350 | 10931
2023-10-03 | 5646 | 4622 | 10268
2023-10-04 | 5590 | 5177 | 10767
2023-10-05 | 5618 | 5408 | 11026
2023-10-06 | 5364 | 4985 | 10349
2023-10-07 | 0 | 0 | 0
2023-10-08 | 0 | 5322 | 5322
2023-10-09 | 4666 | 0 | 4666
2023-10-10 | 5614 | 4597 | 10211
2023-10-11 | 5029 | 5458 | 10487
2023-10-12 | 367 | 7671 | 8038
2023-10-13 | 4856 | 4650 | 9506
2023-10-14 | 4329 | 0 | 4329
2023-10-15 | 0 | 0 | 0
2023-10-16 | 5606 | 8877 | 14483
2023-10-17 | 4351 | 5482 | 9833
2023-10-18 | 10477 | 4514 | 14991
2023-10-19 | 5244 | 9796 | 15040
2023-10-20 | 10733 | 10964 | 21697
2023-10-21 | 10595 | 9512 | 20107
2023-10-22 | 10511 | 4681 | 15192
2023-10-23 | 14017 | 8812 | 22829
2023-10-24 | 5577 | 5501 | 11078
2023-10-25 | 5609 | 4760 | 10369
2023-10-26 | 5636 | 5174 | 10810
2023-10-27 | 5541 | 4360 | 9901
2023-10-28 | 0 | 5300 | 5300
2023-10-29 | 5411 | 0 | 5411
2023-10-30 | 5606 | 10453 | 16059
2023-10-31 | 10607 | 4310 | 14917
Total Flow (L) |  |  | 323917
Average Flow (L/day) |  |  | 10449
Typical Flow (L/day) |  |  | 11568

## Sep 23
September 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-09-01 | 0 | 4409 | 4409
2023-09-02 | 4326 | 0 | 4326
2023-09-03 | 0 | 5174 | 5174
2023-09-04 | 0 | 0 | 0
2023-09-05 | 5532 | 4492 | 10024
2023-09-06 | 5430 | 5642 | 11072
2023-09-07 | 11211 | 0 | 11211
2023-09-08 | 5213 | 5014 | 10227
2023-09-09 | 0 | 0 | 0
2023-09-10 | 0 | 4536 | 4536
2023-09-11 | 5424 | 4918 | 10342
2023-09-12 | 5683 | 0 | 5683
2023-09-13 | 5658 | 5324 | 10982
2023-09-14 | 5069 | 9180 | 14249
2023-09-15 | 9869 | 5207 | 15076
2023-09-16 | 0 | 4474 | 4474
2023-09-17 | 4400 | 0 | 4400
2023-09-18 | 5630 | 4351 | 9981
2023-09-19 | 5698 | 5309 | 11007
2023-09-20 | 5079 | 4342 | 9421
2023-09-21 | 5066 | 8744 | 13810
2023-09-22 | 4347 | 5645 | 9992
2023-09-23 | 5014 | 4909 | 9923
2023-09-24 | 4409 | 4517 | 8926
2023-09-25 | 4578 | 5408 | 9986
2023-09-26 | 9485 | 4810 | 14295
2023-09-27 | 0 | 4952 | 4952
2023-09-28 | 5359 | 5171 | 10530
2023-09-29 | 4372 | 4628 | 9000
2023-09-30 | 4341 | 0 | 4341
Total Flow (L) |  |  | 252349
Average Flow (L/day) |  |  | 8412

## Aug 23
August 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-08-01 | 4498 | 0 | 4498
2023-08-02 | 0 | 0 | 0
2023-08-03 | 0 | 4323 | 4323
2023-08-04 | 4604 | 0 | 4604
2023-08-05 | 0 | 0 | 0
2023-08-06 | 0 | 0 | 0
2023-08-07 | 0 | 0 | 0
2023-08-08 | 0 | 0 | 0
2023-08-09 | 0 | 0 | 0
2023-08-10 | 0 | 4317 | 4317
2023-08-11 | 5510 | 0 | 5510
2023-08-12 | 0 | 0 | 0
2023-08-13 | 4332 | 0 | 4332
2023-08-14 | 0 | 5291 | 5291
2023-08-15 | 0 | 0 | 0
2023-08-16 | 0 | 0 | 0
2023-08-17 | 5044 | 2476 | 7520
2023-08-18 | 0 | 0 | 0
2023-08-19 | 0 | 0 | 0
2023-08-20 | 0 | 0 | 0
2023-08-21 | 4986 | 0 | 4986
2023-08-22 | 0 | 0 | 0
2023-08-23 | 0 | 0 | 0
2023-08-24 | 0 | 5026 | 5026
2023-08-25 | 4804 | 0 | 4804
2023-08-26 | 0 | 5315 | 5315
2023-08-27 | 5078 | 0 | 5078
2023-08-28 | 0 | 4511 | 4511
2023-08-29 | 4899 | 0 | 4899
2023-08-30 | 0 | 4977 | 4977
2023-08-31 | 5698 | 0 | 5698
Total Flow (L) |  |  | 85689
Average Flow (L/day) |  |  | 2764

## Jul 23
July 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-07-01 | 5304 | 0 | 5304
2023-07-02 | 0 | 5010 | 5010
2023-07-03 | 4378 | 0 | 4378
2023-07-04 | 4625 | 4684 | 9309
2023-07-05 | 0 | 5245 | 5245
2023-07-06 | 3984 | 12 | 3996
2023-07-07 | 0 | 5245 | 5245
2023-07-08 | 4252 | 4711 | 8963
2023-07-09 | 5328 | 0 | 5328
2023-07-10 | 0 | 4255 | 4255
2023-07-11 | 4788 | 0 | 4788
2023-07-12 | 0 | 4761 | 4761
2023-07-13 | 4360 | 0 | 4360
2023-07-14 | 0 | 0 | 0
2023-07-15 | 0 | 0 | 0
2023-07-16 | 0 | 0 | 0
2023-07-17 | 0 | 0 | 0
2023-07-18 | 0 | 0 | 0
2023-07-19 | 0 | 4658 | 4658
2023-07-20 | 4582 | 0 | 4582
2023-07-21 | 0 | 0 | 0
2023-07-22 | 0 | 0 | 0
2023-07-23 | 0 | 0 | 0
2023-07-24 | 0 | 0 | 0
2023-07-25 | 0 | 0 | 0
2023-07-26 | 0 | 0 | 0
2023-07-27 | 5550 | 0 | 5550
2023-07-28 | 0 | 0 | 0
2023-07-29 | 0 | 0 | 0
2023-07-30 | 0 | 0 | 0
2023-07-31 | 0 | 5245 | 5245
Total Flow (L) |  |  | 90977
Average Flow (L/day) |  |  | 2935

## Jun 23
June 2023 Daily Flow
Date | Pump 1 Total (L) | Pump 1 (L/day) | Pump 2 Total (L) | Pump 2 (L/day) | Total Daily Flow (L/day)
2023-06-01 | 7035263 | 15056 | 6859778 | 16187 | 31243
2023-06-02 | 7040699 | 5436 | 6859778 | 0 | 5436
2023-06-03 | 7040699 | 0 | 6864712 | 4934 | 4934
2023-06-04 | 7040699 | 0 | 6864712 | 0 | 0
2023-06-05 | 7045016 | 4317 | 6870117 | 5405 | 9722
2023-06-06 | 7050039 | 5023 | 6875460 | 5343 | 10366
2023-06-07 | 7055351 | 5312 | 6880582 | 5122 | 10434
2023-06-08 | 7060738 | 5387 | 6880582 | 0 | 5387
2023-06-09 | 7066134 | 5396 | 6885805 | 5223 | 10619
2023-06-10 | 7066134 | 0 | 6890710 | 4905 | 4905
2023-06-11 | 7070444 | 4310 | 6890710 | 0 | 4310
2023-06-12 | 7075834 | 5390 | 6894928 | 4218 | 9608
2023-06-13 | 7080995 | 5161 | 6899890 | 4962 | 10123
2023-06-14 | 7085349 | 4354 | 6905097 | 5207 | 9561
2023-06-15 | 7090455 | 5106 | 6909994 | 4897 | 10003
2023-06-16 | 7095351 | 4896 | 6914208 | 4214 | 9110
2023-06-17 | 7099609 | 4258 | 6914208 | 0 | 4258
2023-06-18 | 7099609 | 0 | 6918433 | 4225 | 4225
2023-06-19 | 7104802 | 5193 | 6922635 | 4202 | 9395
2023-06-20 | 7109667 | 4865 | 6927815 | 5180 | 10045
2023-06-21 | 7119238 | 9571 | 6937975 | 10160 | 19731
2023-06-22 | 7139273 | 20035 | 6953869 | 15894 | 35929
2023-06-23 | 7148292 | 9019 | 6963912 | 10043 | 19062
2023-06-24 | 7153598 | 5306 | 6968102 | 4190 | 9496
2023-06-25 | 7158606 | 5008 | 6977411 | 9309 | 14317
2023-06-26 | 7169157 | 10551 | 6987956 | 10545 | 21096
2023-06-27 | 7184379 | 15222 | 7002688 | 14732 | 29954
2023-06-28 | 7199389 | 15010 | 7012184 | 9496 | 24506
2023-06-29 | 7204751 | 5362 | 7021811 | 9627 | 14989
2023-06-30 | 7209024 | 4273 | 7026883 | 5072 | 9345
Total Flow (L) |  |  |  |  | 372109
Average Flow (L/day) |  |  |  |  | 12404

## May 23
May 2023 Daily Flow
Date | Pump 1 Total (L) | Pump 1 (L/day) | Pump 2 Total (L) | Pump 2 (L/day) | Total Daily Flow (L/day)
2023-05-01 | 6866950 | 5226 | 6693016 | 4322 | 9548
2023-05-02 | 6872112 | 5162 | 6697336 | 4320 | 9482
2023-05-03 | 6877452 | 5340 | 6701927 | 4591 | 9931
2023-05-04 | 6882684 | 5232 | 6707212 | 5285 | 10517
2023-05-05 | 6887584 | 4900 | 6712528 | 5316 | 10216
2023-05-06 | 6887584 | 0 | 6717877 | 5349 | 5349
2023-05-07 | 6892446 | 4862 | 6717877 | 0 | 4862
2023-05-08 | 6897814 | 5368 | 6723168 | 5291 | 10659
2023-05-09 | 6903235 | 5421 | 6727963 | 4795 | 10216
2023-05-10 | 6908421 | 5186 | 6733010 | 5047 | 10233
2023-05-11 | 6913028 | 4607 | 6737592 | 4582 | 9189
2023-05-12 | 6917412 | 4384 | 6742732 | 5140 | 9524
2023-05-13 | 6921852 | 4440 | 6742732 | 0 | 4440
2023-05-14 | 6921852 | 0 | 6747653 | 4921 | 4921
2023-05-15 | 6926409 | 4557 | 6753163 | 5510 | 10067
2023-05-16 | 6930754 | 4345 | 6758620 | 5457 | 9802
2023-05-17 | 6935076 | 4322 | 6764044 | 5424 | 9746
2023-05-18 | 6939680 | 4604 | 6769576 | 5532 | 10136
2023-05-19 | 6944635 | 4955 | 6775058 | 5482 | 10437
2023-05-20 | 6949580 | 4945 | 6775058 | 0 | 4945
2023-05-21 | 6949580 | 0 | 6780102 | 5044 | 5044
2023-05-22 | 6955134 | 5554 | 6780102 | 0 | 5554
2023-05-23 | 6966018 | 10884 | 6791045 | 10943 | 21827
2023-05-24 | 6970341 | 4323 | 6801855 | 10810 | 15133
2023-05-25 | 6975702 | 5361 | 6806144 | 4289 | 9650
2023-05-26 | 6980479 | 4777 | 6810646 | 4502 | 9279
2023-05-27 | 6985773 | 5294 | 6810646 | 0 | 5294
2023-05-28 | 6985773 | 0 | 6815012 | 4366 | 4366
2023-05-29 | 6991280 | 5507 | 6819285 | 4273 | 9780
2023-05-30 | 7000227 | 8947 | 6829497 | 10212 | 19159
2023-05-31 | 7020207 | 19980 | 6843591 | 14094 | 34074
Total Flow (L) |  |  |  |  | 313380
Average Flow (L/day) |  |  |  |  | 10109

## Apr 23
April 2023 Daily Flow
Date | Pump 1 Total (L) | Pump 1 (L/day) | Pump 2 Total (L) | Pump 2 (L/day) | Total Daily Flow (L/day)
2023-04-01 | 6733547 | 0 | 6562172 | 5223 | 5223
2023-04-02 | 6737854 | 4307 | 6567173 | 5001 | 9308
2023-04-03 | 6742673 | 4819 | 6571891 | 4718 | 9537
2023-04-04 | 6747036 | 4363 | 6577357 | 5466 | 9829
2023-04-05 | 6755682 | 8646 | 6582769 | 5412 | 14058
2023-04-06 | 6761235 | 5553 | 6592524 | 9755 | 15308
2023-04-07 | 6766754 | 5519 | 6592524 | 0 | 5519
2023-04-08 | 6766754 | 0 | 6597846 | 5322 | 5322
2023-04-09 | 6772135 | 5381 | 6597846 | 0 | 5381
2023-04-10 | 6772249 | 114 | 6602844 | 4998 | 5112
2023-04-11 | 6776960 | 4711 | 6608148 | 5304 | 10015
2023-04-12 | 6782347 | 5387 | 6613016 | 4868 | 10255
2023-04-13 | 6786858 | 4511 | 6618498 | 5482 | 9993
2023-04-14 | 6791655 | 4797 | 6623607 | 5109 | 9906
2023-04-15 | 6797131 | 5476 | 6623607 | 0 | 5476
2023-04-16 | 6797131 | 0 | 6628405 | 4798 | 4798
2023-04-17 | 6802102 | 4971 | 6633206 | 4801 | 9772
2023-04-18 | 6806767 | 4665 | 6637899 | 4693 | 9358
2023-04-19 | 6811197 | 4430 | 6642638 | 4739 | 9169
2023-04-20 | 6816436 | 5239 | 6647232 | 4594 | 9833
2023-04-21 | 6821382 | 4946 | 6647232 | 0 | 4946
2023-04-22 | 6825933 | 4551 | 6651909 | 4677 | 9228
2023-04-23 | 6825933 | 0 | 6657268 | 5359 | 5359
2023-04-24 | 6830647 | 4714 | 6662097 | 4829 | 9543
2023-04-25 | 6841886 | 11239 | 6667684 | 5587 | 16826
2023-04-26 | 6847054 | 5168 | 6673080 | 5396 | 10564
2023-04-27 | 6852237 | 5183 | 6677803 | 4723 | 9906
2023-04-28 | 6856646 | 4409 | 6683103 | 5300 | 9709
2023-04-29 | 6856646 | 0 | 6688694 | 5591 | 5591
2023-04-30 | 6861724 | 5078 | 6688694 | 0 | 5078
Total Flow (L) |  |  |  |  | 259922
Average Flow (L/day) |  |  |  |  | 8664

## Mar 23
March 2023 Daily Flow
Date | Pump 1 Total (L) | Pump 1 (L/day) | Pump 2 Total (L) | Pump 2 (L/day) | Total Daily Flow (L/day)
2023-03-01 | 6587893 | 5303 | 6420921 | 4729 | 10032
2023-03-02 | 6593166 | 5273 | 6420921 | 0 | 5273
2023-03-03 | 6593166 | 0 | 6426178 | 5257 | 5257
2023-03-04 | 6598450 | 5284 | 6426178 | 0 | 5284
2023-03-05 | 6598450 | 0 | 6431473 | 5295 | 5295
2023-03-06 | 6606856 | 8406 | 6435839 | 4366 | 12772
2023-03-07 | 6611965 | 5109 | 6440232 | 4393 | 9502
2023-03-08 | 6617265 | 5300 | 6444990 | 4758 | 10058
2023-03-09 | 6621967 | 4702 | 6449507 | 4517 | 9219
2023-03-10 | 6626666 | 4699 | 6454786 | 5279 | 9978
2023-03-11 | 6626666 | 0 | 6459201 | 4415 | 4415
2023-03-12 | 6631932 | 5266 | 6459201 | 0 | 5266
2023-03-13 | 6631932 | 0 | 6464236 | 5035 | 5035
2023-03-14 | 6637282 | 5350 | 6464236 | 0 | 5350
2023-03-15 | 6637282 | 0 | 6468997 | 4761 | 4761
2023-03-16 | 6642632 | 5350 | 6469163 | 166 | 5516
2023-03-17 | 6647152 | 4520 | 6469163 | 0 | 4520
2023-03-18 | 6647152 | 0 | 6474411 | 5248 | 5248
2023-03-19 | 6652443 | 5291 | 6474411 | 0 | 5291
2023-03-20 | 6657018 | 4575 | 6479677 | 5266 | 9841
2023-03-21 | 6662359 | 5341 | 6489251 | 9574 | 14915
2023-03-22 | 6667665 | 5306 | 6494579 | 5328 | 10634
2023-03-23 | 6672549 | 4884 | 6499920 | 5341 | 10225
2023-03-24 | 6681784 | 9235 | 6505167 | 5247 | 14482
2023-03-25 | 6681784 | 0 | 6510039 | 4872 | 4872
2023-03-26 | 6687204 | 5420 | 6510039 | 0 | 5420
2023-03-27 | 6692273 | 5069 | 6519647 | 9608 | 14677
2023-03-28 | 6697533 | 5260 | 6524996 | 5349 | 10609
2023-03-29 | 6706262 | 8729 | 6530176 | 5180 | 13909
2023-03-30 | 6717122 | 10860 | 6545914 | 15738 | 26598
2023-03-31 | 6733547 | 16425 | 6556949 | 11035 | 27460
Total Flow (L) |  |  |  |  | 291714
Average Flow (L/day) |  |  |  |  | 9410

## Feb 23
February 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-02-01 | 4668 | 4097 | 8765
2023-02-02 | 5088 | 4317 | 9405
2023-02-03 | 4911 | 4181 | 9092
2023-02-04 | 0 | 4045 | 4045
2023-02-05 | 4280 | 0 | 4280
2023-02-06 | 4801 | 5122 | 9923
2023-02-07 | 2920 | 5066 | 7986
2023-02-08 | 6475 | 5161 | 11636
2023-02-09 | 5229 | 5060 | 10289
2023-02-10 | 4899 | 4233 | 9132
2023-02-11 | 0 | 5119 | 5119
2023-02-12 | 4755 | 0 | 4755
2023-02-13 | 5303 | 5208 | 10511
2023-02-14 | 4841 | 4692 | 9533
2023-02-15 | 4853 | 4132 | 8985
2023-02-16 | 4302 | 5044 | 9346
2023-02-17 | 4868 | 5042 | 9910
2023-02-18 | 0 | 4400 | 4400
2023-02-19 | 4178 | 0 | 4178
2023-02-20 | 0 | 4304 | 4304
2023-02-21 | 5282 | 0 | 5282
2023-02-22 | 5328 | 5189 | 10517
2023-02-23 | 0 | 5214 | 5214
2023-02-24 | 5257 | 4730 | 9987
2023-02-25 | 4542 | 0 | 4542
2023-02-26 | 0 | 4597 | 4597
2023-02-27 | 4184 | 4801 | 8985
2023-02-28 | 4295 | 4949 | 9244
Total Flow (L) |  |  | 213962
Average Flow (L/day) |  |  | 7642

## Jan 23
January 2023 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2023-01-01 | 4894 | 0 | 4894
2023-01-02 | 0 | 4828 | 4828
2023-01-03 | 0 | 0 | 0
2023-01-04 | 8254 | 28 | 8282
2023-01-05 | 0 | 5060 | 5060
2023-01-06 | 4788 | 0 | 4788
2023-01-07 | 0 | 4286 | 4286
2023-01-08 | 0 | 0 | 0
2023-01-09 | 5121 | 5143 | 10264
2023-01-10 | 8924 | 4332 | 13256
2023-01-11 | 4387 | 4193 | 8580
2023-01-12 | 0 | 5125 | 5125
2023-01-13 | 5196 | 4748 | 9944
2023-01-14 | 5022 | 0 | 5022
2023-01-15 | 0 | 4064 | 4064
2023-01-16 | 5177 | 0 | 5177
2023-01-17 | 4841 | 10255 | 15096
2023-01-18 | 5075 | 5146 | 10221
2023-01-19 | 5085 | 4986 | 10071
2023-01-20 | 4418 | 4893 | 9311
2023-01-21 | 4563 | 0 | 4563
2023-01-22 | 0 | 4924 | 4924
2023-01-23 | 4777 | 4116 | 8893
2023-01-24 | 5118 | 4058 | 9176
2023-01-25 | 5146 | 0 | 5146
2023-01-26 | 0 | 5137 | 5137
2023-01-27 | 4755 | 0 | 4755
2023-01-28 | 0 | 4073 | 4073
2023-01-29 | 4085 | 0 | 4085
2023-01-30 | 4122 | 4064 | 8186
2023-01-31 | 4502 | 4067 | 8569
Total Flow (L) |  |  | 205776
Average Flow (L/day) |  |  | 6638

## Dec 22
December 2022 Daily Flow
Date | Disposal 1 (L/day) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2022-12-01 | 4859 | 4631 | 9490
2022-12-02 | 4375 | 0 | 4375
2022-12-03 | 4086 | 4366 | 8452
2022-12-04 | 4890 | 0 | 4890
2022-12-05 | 4970 | 4230 | 9200
2022-12-06 | 4968 | 4795 | 9763
2022-12-07 | 5124 | 5063 | 10187
2022-12-08 | 5106 | 5023 | 10129
2022-12-09 | 5159 | 4310 | 9469
2022-12-10 | 0 | 5035 | 5035
2022-12-11 | 5112 | 0 | 5112
2022-12-12 | 5118 | 4943 | 10061
2022-12-13 | 5149 | 5041 | 10190
2022-12-14 | 5137 | 5047 | 10184
2022-12-15 | 4002 | 5054 | 9056
2022-12-16 | 5143 | 4240 | 9383
2022-12-17 | 0 | 4433 | 4433
2022-12-18 | 4292 | 0 | 4292
2022-12-19 | 4453 | 4860 | 9313
2022-12-20 | 0 | 5026 | 5026
2022-12-21 | 4085 | 5075 | 9160
2022-12-22 | 9959 | 4939 | 14898
2022-12-23 | 0 | 4212 | 4212
2022-12-24 | 4431 | 0 | 4431
2022-12-25 | 0 | 4076 | 4076
2022-12-26 | 4110 | 0 | 4110
2022-12-27 | 0 | 4228 | 4228
2022-12-28 | 4930 | 0 | 4930
2022-12-29 | 0 | 4051 | 4051
2022-12-30 | 4298 | 0 | 4298
2022-12-31 | 0 | 4804 | 4804
Total Flow (L) |  |  | 221238
Average Flow (L/day) |  |  | 7137

## Nov 22
November 2022 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2022-11-01 | 6134390 | 5066 | 5984617 | 4995 | 10061
2022-11-02 | 6139022 | 4632 | 5989631 | 5014 | 9646
2022-11-03 | 6143455 | 4433 | 5994284 | 4653 | 9086
2022-11-04 | 6147649 | 4194 | 5998400 | 4116 | 8310
2022-11-05 | 6147649 | 0 | 6003179 | 4779 | 4779
2022-11-06 | 6152579 | 4930 | 6003179 | 0 | 4930
2022-11-07 | 6152579 | 0 | 6008143 | 4964 | 4964
2022-11-08 | 6157484 | 4905 | 6012432 | 4289 | 9194
2022-11-09 | 6167043 | 9559 | 6012444 | 12 | 9571
2022-11-10 | 6172152 | 5109 | 6016749 | 4305 | 9414
2022-11-11 | 6177249 | 5097 | 6021765 | 5016 | 10113
2022-11-12 | 6181340 | 4091 | 6026027 | 4262 | 8353
2022-11-13 | 6181340 | 0 | 6030926 | 4899 | 4899
2022-11-14 | 6185999 | 4659 | 6035542 | 4616 | 9275
2022-11-15 | 6190710 | 4711 | 6039788 | 4246 | 8957
2022-11-16 | 6195104 | 4394 | 6044829 | 5041 | 9435
2022-11-17 | 6199988 | 4884 | 6049454 | 4625 | 9509
2022-11-18 | 6204601 | 4613 | 6054190 | 4736 | 9349
2022-11-19 | 6209284 | 4683 | 6054190 | 0 | 4683
2022-11-20 | 6209284 | 0 | 6058978 | 4788 | 4788
2022-11-21 | 6218704 | 9420 | 6063282 | 4304 | 13724
2022-11-22 | 6223224 | 4520 | 6067898 | 4616 | 9136
2022-11-23 | 6228309 | 5085 | 6071984 | 4086 | 9171
2022-11-24 | 6232391 | 4082 | 6080996 | 9012 | 13094
2022-11-25 | 6236751 | 4360 | 6080996 | 0 | 4360
2022-11-26 | 6240833 | 4082 | 6085060 | 4064 | 8146
2022-11-27 | 6240833 | 0 | 6089759 | 4699 | 4699
2022-11-28 | 6245430 | 4597 | 6093792 | 4033 | 8630
2022-11-29 | 6250401 | 4971 | 6097893 | 4101 | 9072
2022-11-30 | 6255325 | 4924 | 6102481 | 4588 | 9512
Total Flow (L) |  |  |  |  | 248860
Average Flow (L/day) |  |  |  |  | 8295

## Oct 22
October 2022 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2022-10-01 | 5970567 | 13835 | 5826513 | 14245 | 28080
2022-10-02 | 5980615 | 10048 | 5839371 | 12858 | 22906
2022-10-03 | 5995384 | 14769 | 5849265 | 9894 | 24663
2022-10-04 | 6000420 | 5036 | 5854226 | 4961 | 9997
2022-10-05 | 6004533 | 4113 | 5863331 | 9105 | 13218
2022-10-06 | 6019009 | 14476 | 5876766 | 13435 | 27911
2022-10-07 | 6032872 | 13863 | 5886685 | 9919 | 23782
2022-10-08 | 6032872 | 0 | 5890798 | 4113 | 4113
2022-10-09 | 6036898 | 4026 | 5890798 | 0 | 4026
2022-10-10 | 6036898 | 0 | 5890798 | 0 | 0
2022-10-11 | 6046608 | 9710 | 5899795 | 8997 | 18707
2022-10-12 | 6051634 | 5026 | 5904808 | 5013 | 10039
2022-10-13 | 6056693 | 5059 | 5909042 | 4234 | 9293
2022-10-14 | 6061365 | 4672 | 5918532 | 9490 | 14162
2022-10-15 | 6065598 | 4233 | 5918532 | 0 | 4233
2022-10-16 | 6065598 | 0 | 5922596 | 4064 | 4064
2022-10-17 | 6072748 | 7150 | 5927283 | 4687 | 11837
2022-10-18 | 6077691 | 4943 | 5931624 | 4341 | 9284
2022-10-19 | 6082670 | 4979 | 5935654 | 4030 | 9009
2022-10-20 | 6087706 | 5036 | 5939724 | 4070 | 9106
2022-10-21 | 6092294 | 4588 | 5943991 | 4267 | 8855
2022-10-22 | 6092294 | 0 | 5948946 | 4955 | 4955
2022-10-23 | 6097261 | 4967 | 5948946 | 0 | 4967
2022-10-24 | 6101858 | 4597 | 5953762 | 4816 | 9413
2022-10-25 | 6106677 | 4819 | 5957900 | 4138 | 8957
2022-10-26 | 6111611 | 4934 | 5962165 | 4265 | 9199
2022-10-27 | 6116069 | 4458 | 5966429 | 4264 | 8722
2022-10-28 | 6121154 | 5085 | 5971152 | 4723 | 9808
2022-10-29 | 6121154 | 0 | 5975216 | 4064 | 4064
2022-10-30 | 6125217 | 4063 | 5975216 | 0 | 4063
2022-10-31 | 6129324 | 4107 | 5979622 | 4406 | 8513
Total Flow (L) |  |  |  |  | 339946
Average Flow (L/day) |  |  |  |  | 10966

## Sep 22
September 2022 Daily Flow
Date | Pump 1 Total (L) | Disposal 1 (L/day) | Pump 2 Total (L) | Disposal 2 (L/day) | Total Daily Flow (L/day)
2022-09-01 | 5790451 | 4200 | 5644251 | 0 | 4200
2022-09-02 | 5790451 | 0 | 5648969 | 4718 | 4718
2022-09-03 | 5794484 | 4033 | 5648969 | 0 | 4033
2022-09-04 | 5794484 | 0 | 5652922 | 3953 | 3953
2022-09-05 | 5799479 | 4995 | 5652922 | 0 | 4995
2022-09-06 | 5803496 | 4017 | 5657833 | 4911 | 8928
2022-09-07 | 5807714 | 4218 | 5662579 | 4746 | 8964
2022-09-08 | 5811886 | 4172 | 5667287 | 4708 | 8880
2022-09-09 | 5816024 | 4138 | 5677024 | 9737 | 13875
2022-09-10 | 5839386 | 23362 | 5700507 | 23483 | 46845
2022-09-11 | 5864293 | 24907 | 5720743 | 20236 | 45143
2022-09-12 | 5878098 | 13805 | 5738845 | 18102 | 31907
2022-09-13 | 5883077 | 4979 | 5742893 | 4048 | 9027
2022-09-14 | 5886694 | 3617 | 5747315 | 4422 | 8039
2022-09-15 | 5890933 | 4239 | 5751635 | 4320 | 8559
2022-09-16 | 5895111 | 4178 | 5756090 | 4455 | 8633
2022-09-17 | 5899536 | 4425 | 5756090 | 0 | 4425
2022-09-18 | 5899536 | 0 | 5760946 | 4856 | 4856
2022-09-19 | 5903856 | 4320 | 5765343 | 4397 | 8717
2022-09-20 | 5908678 | 4822 | 5765343 | 0 | 4822
2022-09-21 | 5913596 | 4918 | 5770280 | 4937 | 9855
2022-09-22 | 5918643 | 5047 | 5774624 | 4344 | 9391
2022-09-23 | 5923432 | 4789 | 5779437 | 4813 | 9602
2022-09-24 | 5923432 | 0 | 5784266 | 4829 | 4829
2022-09-25 | 5928223 | 4791 | 5784266 | 0 | 4791
2022-09-26 | 5928223 | 0 | 5789267 | 5001 | 5001
2022-09-27 | 5936826 | 8603 | 5794246 | 4979 | 13582
2022-09-28 | 5937060 | 234 | 5799226 | 4980 | 5214
2022-09-29 | 5946658 | 9598 | 5803845 | 4619 | 14217
2022-09-30 | 5956732 | 10074 | 5812268 | 8423 | 18497
Total Flow (L) |  |  |  |  | 338498
Average Flow (L/day) |  |  |  |  | 11283